## Calculator
Model | Internal power | Quantity | Sensing Power | Quantity of sensors | 24 I/O remaining power | 40I/O main circuit remaining power | 辅路计算中程1 | 60I/O main circuit remaining power | 辅路计算中程2 | NOTE
LX3V-16EX | 1.2 | 1 | 2 | 0 | 16.6 | 39.6 | 17 | 37.6 | 17 | Software limitations, a PLC can only receive a maximum of 16 extension modules.
LX3V-16EYR | 3.6 | 0 | - | -
LX3V-16EYT/4PG | 1.2 | 1 | - | -
LX3V-4AD | 0.7 | 0 | 1.7 | 0
LX3V-4PT | 0.7 | 0 | 1.7 | 0
LX3V-4TC/8iTC | 0.7 | 0 | 1.7 | 0
LX3V-4DA | 0.7 | 0 | 4 | 0
LX3V-1WT | 0.7 | 0 | 3 | 0
LX3V-2AD2DA-BD | 1.8 | 0 | - | - |  | 40I/O Auxiliary remaining power |  | 6040I/O Auxiliary remaining power
LX3V-2RS485-BD | 0.8 | 0 | - | - |  | 17 |  | 17
LX3V-24MX | 6 | - | 1.8 | 0
LX3V-40MX | 8 | - | 3 | 0
LX3V-60MX | 10 | - | 4.5 | 0

## Directions for use
Instructions for use of simple calculator for host/expansion module scheme This table is calculated for 3V models 24, 40, and 60 at the same time, depending on which model is configured. Detailed explanation of use: all numeric tables containing orange can be entered. Table power value unit: Watt Model: Product name. Internal power: the maximum power of the product connected to the internal power supply of the host (not the 24V part of the terminal block), such as the expansion module cable, BD, the host itself, etc. Number of connections: refers to how many modules are connected to the host, and write 0 without connection. Among them, BD module can only be connected to 1, then fill in 0 or 1. Sensing power: the maximum power of the product connected to the 24V power supply part (auxiliary circuit) of the host terminal block, such as the analog power supply on the right module, the X port of the EX module, etc. Generally, it is not recommended for customers to connect, it is best to use self-provided 24V adapter. Number of sensors: Refers to how many modules "need to be connected to the 24V power supply part of the host terminal", and write 0 for unused modules. The sensor of the host refers to the X port (full contact is lit), it has only one, then fill in 0 or 1.