Modbus Free

-LX6V

V1.0

Website: http://www.we-con.com.cn/en

Phone: 86-591-8786886

Overview

This document describes the [Modbus Free] protocol,according this protocol,user can connect PLC global variable to modbus register.Then use modbus connect other device with PLC global variable introduces it in two parts:

⚫  Protocol Description

⚫  Software Configurations of Modbus Free

I Protocol Description

1.1What is Modbus?

Modbus is a data communications protocol originally published by Modicon (now Schneider Electric) in 1979 for use with its programmable logic controllers (PLCs). It has become the most popular open standard communication protocol and is now a commonly available means of connecting industrial electronic devices.

1.2MODBUS RTU message format

| Device address | Function code | Data format | CRC check |
| --- | --- | --- | --- |
| 8 bit | 8 bit | N x 8 bit | 2 x 8 bit |

Device address：

The Slave ID of the modbus slave device.

Function code:

Operate the slave station according to the function code.

| Function code | Function |
| --- | --- |
| 01 | Read the coil state |
| 05 | Set the coil state |
| 03 | Read the input register value |
| 06 | Write the input register value |
| 0F | write multiple coils |
| 10 | Write multiple registers |
| 02 | Read the discrete input state |
| 04 | Read the holding register value |

Data format:

Data content, including register/coil address + data

CRC check:

Calculate CRC check based on root data to determine whether the data is correct.

ⅡSoftware Configurations of Modbus Free

2.1 PLC Software

Figure 2-1

Notice:Prior to this version, modbus free protocol can not use.

2.2 Create variable

Figure 2-2

First,right click [Modbus mapping table] in program tree,create a modbus table in project.

Figure 2-3

Right click the global variable,add the variable to modbus mapping list.

| Data format | Modbus format |
| --- | --- |
| BOOL | Coil,Discrete input |
| BYTE | Input register,Keep register |
| WORD,DWORD,LWORD | Input register,Keep register |
| SINT,USINT,INT,UINT,DINT,UDINT | Input register,Keep register |
| REAL,LREAL | Input register,Keep register |
| STRING | Can not support |

Figure 2-4

- Name of variable.

- Data type of variable.

- Modbus address of variable.

Such as: If I need read state of [GVL.ADD_triger].I need read [coil] address 0.

Then use function code [01] and [05] to do read and write to this address.

Figure 2-5

2.3 Modbus slave

Notice: Modbus free protocol can only use in PLC as slave.

2.3.1 Modbus RTU

- Figure 2-6

[Parameter]-[PLC parameter]-[COM1 settings]-Protocol[MODBUS FREE RTU]

2.3.2 Modbus TCP

- Figure 2-7

Right click [Ethernet]-[New]-Protocol type[ModbusFreeTCP Slave]

Notice: Modbus TCP IP is the PLC IP.

Notice: Modbus TCP IP can use with Modbus RTU at the same time.Use the same address list.