Delta DVP Ethernet

Website: http://www.we-con.com.cn/en

Technical Support: support@we-con.com.cn

Skype: fcwkkj

Phone: 86-591-87868869	EXT 88

1.Communication settings

VBOX Setting:

Configuration>>Communication>>Add new port>>Set the communication parameter as below:

Select:Port--->”Ethernet”

- Device Type--->”Delta”

- Protocol--->”Delta_AS300_TCP”

Set IP Address as PLC’s IP, such as “192.168.1.3”
Note: Ensure that PLC IP and V-box IP are in the same network segment “192.168.1.xx”
PLC setting:

Basic settings>>Network settings>>IP set as 192.168.1.3

2.Operation Steps

2.1 RS485 serial port communication

2.1.1 VBOX communication settings

Configuration>>Communication>>Add new port>>Set the communication parameter as below:

2.1.2 PLC communication settings

STEP 7-MicroWIN SMART:

Main>>system block>>RS485 port, change the baud rate to 187.5kbps

2.1.3 Establish connection

The VBOX uses the COM1 port, and the PLC uses the RS485 port

COM1 port pin 1 is connected to RS485 port pin 3

COM1 port pin 6 is connected to RS485 port pin 8

The pin connections are as follows:

H series VBOX COM1 Pin Definition

2.2 Ethernet port communication

2.2.1 VBOX communication settings

Configuration>>Communication>>Add new port>>Set the communication parameter as below:

IP Address ”192.168.1.202” is PLC IP address, need to be the same network segment as VBOX.

2.2.2 IP settings

VBOX: Networking configuration>>LAN IP set as”192.168.1.xx”(make sure there is no IP conflic)

STEP 7-MicroWIN SMART:

Main_Communication_Search CPU, find CPU (if you need to change IP, click edit, modify IP, click set), click OK

Note: The IP of the PLC must be consistent with the IP set on the HMI(communication>>TCP/IP parameters)

2.2.3 Establish connection

Use a ethernet cable to connect the VBOX and PLC on the same Local Area Network, or connect the VBOX to PLC directly with ethernet cable. Both methods can be connected.